CHAPTER 36

Title: Fire Safety

Issuance Date: Prior to 2011

Instruction:  This chapter is revised to include the new Occupational Safety and Health Administration (OSHA) standard, 29 Code of Federal Regulations (CFR) 1910.39, and to include training and inspection requirements for fire extinguishers.

Approving Official: Carol F. Aten, Chief, Office of Administrative Policy and Services

- Purpose.  This chapter specifies the minimum Occupational Safety and Health Program (Program) requirements for protecting Department of the Interior (Department or DOI), U.S. Geological Survey (Bureau or USGS), and public property and persons from the adverse effects of fires.

- Authority and References.

- 29 CFR 1910.39, Fire Prevention Plans, and Subpart L, Fire Protection (1910.155, 1910.156, 1910.157, 1910.158, 1910.159, 1910.160, 1910.161, 1910.162, 1910.163, 1910.164).

- National Fire Codes (NFPA 1 Uniform Fire Code and NFPA 101 Life Safety Code).

- 1997 Uniform Building Code.

- 41 CFR 102-74, Facility Management

- USGS Requirements.

- Establish written fire prevention and protection requirements that:

- Provide for accidental fires and related fire losses to be minimized, if not eliminated.  The written fire prevention and protection plan, which may be included in the Occupant Emergency Plan, should include:

- A list of all major fire hazards, proper handling and storage procedures for hazardous materials, potential ignition sources and their control, and the type of fire protection equipment necessary to control each major hazard;

- Procedures to control accumulations of flammable and combustible waste materials;

- Procedures for regular maintenance of safeguards installed on heat-producing equipment to prevent the accidental ignition of combustible materials;

- The name or job title of employees responsible for maintaining equipment to prevent or control sources of ignition or fires; and

- The name or job title of employees responsible for the control of fuel source hazards.

- Provide for fires to be promptly detected, reported, controlled, extinguished, and investigated.

- Establish abatement procedures.

- Provide for the safe evacuation of building occupants through the establishment, maintenance, and implementation and annual updating of Occupant Emergency Plans.

- The USGS will abide by the requirements contained in 41 CFR 102-74.  In those General Services Administration (GSA)-leased buildings where USGS is the major tenant, then the USGS will have the responsibility to prepare the required Occupant Emergency Plans.  In those GSA-leased buildings where USGS is not the major tenant or lead agency, USGS will assist the lead agency in completion of the required plan.

- Participate in at least one fire drill per year.

- Keep all exits, accesses to exits and accesses to emergency equipment clear at all times.

- Prohibit hazardous, explosive, or combustible materials in buildings unless authorized by appropriate agency officials and by GSA unless protective arrangements determined necessary by GSA have been provided.

- Ensure that all draperies, curtains or other hanging materials are of non-combustible or flame-resistant fabric and that freestanding partitions and space dividers are limited combustible, and their fabric coverings are flame resistant.

- Inspection and Testing.

- Require fire detection and suppression systems/equipment to be inspected at least annually by qualified persons and maintained in safe operating condition.

- In GSA-leased space, this requirement is part of the lease and is the responsibility of the building owner.

- In USGS space, this requirement is the responsibility of management in charge of the specific facility.

- Require portable extinguishers be visually inspected monthly.

- Require portable fire extinguishers be subjected to an annual maintenance check. Stored pressure extinguishers do not require an internal examination.  Prepare a written record of the annual maintenance date and retain this record for one year after the last entry or the life of the shell, whichever is less.

- Require portable extinguishers be hydrostatically tested at the intervals listed in Table L-1 of 29 CFR 1910.157 or whenever they show new evidence of corrosion or mechanical injury. Portable extinguishers are not to be hydrostatically tested –

- When the unit has been repaired by soldering, welding, brazing, or use of patching compounds.

- When the cylinder or shell threads are damaged.

- When there is corrosion that has caused pitting, including corrosion under removable name plate assemblies.

- When the extinguisher has been burned in a fire.

- When a calcium chloride extinguishing agent has been used in a stainless-steel shell.

- Require preoccupancy and periodic inspections to be performed as covered in the Department of the Interior Part 485 of the Department Manual (DM) Chapter 6.

- Train personnel in the fire hazards to which they are exposed, those parts of the fire prevention plan necessary for self-protection, the basics of fire prevention, fire extinguisher use, emergency response, and Occupant Emergency Plan procedures.

- Special training will be provided for fire brigade members as necessary to enable them to safely execute their assigned duties. When USGS organizational units elect to assign personnel to a fire brigade, this decision will be coordinated with the Regional Safety Officer and Regional Safety Manager, as applicable.  If such a unit is formed, it will conform to the requirements of 29 CFR 1910.156, Fire Brigades.

- Employees that are expected to use fire extinguishers must be trained in their use upon initial assignment and at least annually.

- Use the National Fire Protection Association (NFPA) Life Safety Code 101 as the minimum criteria for life safety features in occupied USGS space, unless some other more stringent code is applicable.  See Appendix A for a suggested NFPA fire safety code compliance inspection checklist.

- Secure the services of a qualified fire protection specialist to evaluate USGS fire prevention and protection program, as needed.

- Maintain the following records:

- Acceptance test reports and inspection reports of the fire protection systems/equipment as required by applicable NFPA standards.

- Periodic test reports and inspection reports of fire protection systems/equipment for the last 12 years as required by applicable NFPA standards.

- Manufacturers’ operating instructions for life of fire systems.

- Abatement plans and reports of corrective measures for the last 3 years.

- In GSA-leased space, the subject reports and records will be maintained by the building owner.

- In USGS space, these requirements are the responsibility of management in charge of the specific facility.

CHAPTER 36, APPENDIX A

NFPA Compliance Inspection Checklist

See the USGS internal safety Web site for NFPA (National Fire Protection Association)

Codes on-line at http://www.nfpacodesonline.com/.

Contact OSHMB if you require additional assistance.

| # USGS FIRE INSPECTION/ANALYSIS # Inspection Performed By: _____________________ Date of Inspection:___________ |  |  |
| --- | --- | --- |
| ## Part I Administration |  |  |
| ## Region: |  |  |
| ## Organization name/location: |  |  |
| ## Building number: |  |  |
| ## Building name: |  |  |
| ## Building address: |  |  |
| ## Primary occupant: |  |  |
| ## Building manager: |  |  |
| ## Part II Values to be Protected |  |  |
| ## (1) Historic Status (Check One) |  |  |
| ## A | ## National Historic Landmark |  |
| ## B | ## National/State significance |  |
| ## C | ## Local significance |  |
| ## D | ## No significance |  |
| ## (2) Significance of Contents (Check One) |  |  |
| ## A | ## Irreplaceable |  |
| ## B | ## Replaceable |  |
| ## C | ## Reproducible |  |
| ## D | ## Expendable |  |
| ## (3) Ownership Status (Check One) |  |  |
| ## A | ## USGS owned and managed |  |
| ## B | ## USGS owned managed by other |  |
| ## C | ## USGS occupied managed by other |  |
| ## D | ## Multiple use-area managed separately |  |
| ## (4) Mission Significance (Check One) |  |  |
| ## A | ## Mission critical |  |
| ## B | ## Mission essential |  |
| ## C | ## Mission enhancing |  |

| ## (5) Construction (Check predominant construction type ref: NFPA 220 Chapter 3) |  |  |  |
| --- | --- | --- | --- |
| ## A |  | ## Type I |  |
| ## B |  | ## Type II |  |
| ## C |  | ## Type III |  |
| ## D |  | ## Type IV |  |
| ## E |  | ## Type V |  |
| ## F |  | ## Number of Floors:_____________ Total square footage: ______ × _____ = _______ft2 |  |
| ## Part III General Fire Safety |  |  |  |
| (1) Fire Prevention |  |  |  |
| A | Building Services: Yes N/A |  |  |
| B | Electricity Natural Gas LPG Water Other: _____________________ |  |  |
| C | Utilities in good visual working order: Yes No Comment: __________________ |  |  |
| D | Elevators: Yes No Fire Service Control: Yes No Elevator recall: Yes No |  |  |
| E | Heat Type: Natural Gas LPG Oil Electric N/A Other: _____________________ In good visual working order: Yes No |  |  |
| F | Wood or Coal Burning Devices: Yes No Operational: Yes No |  |  |
| G | Properly Installed & Maintained: Yes No N/A Fuel stored properly: Yes No N/A |  |  |
| H | Combustible materials adequate distance from device: Yes No N/A |  |  |
| I | Proper clearance of pipes or flue: Yes No N/A |  |  |
| J | Emergency Generator: Yes No Date tested: _________________ Date of last full load test: _____________ In automatic position: Yes No Tested by: ____________________________________ |  |  |
| K | Fire Pump: Yes No Date tested: __________________ Date of last flow test: ____________ In automatic position: Yes No Tested by: _________________________ |  |  |
| M | Extension cords used as substitution for permanent wiring: Yes No Not Observed |  |  |
| N | Electrical panels clearly accessible: Yes No |  |  |
| O | Electrical circuits clearly identified: Yes No |  |  |
| P | Number of portable heaters: _______ Properly used: Yes No Not Observed |  |  |
| R | Areas free of excessive combustibles: Yes No |  |  |
| S | Proper disposal of wood stove or fireplace ash: Yes No N/A |  |  |
| T | Smoking regulated in common areas: Yes No |  |  |
| V | Proper use of open flame devices: (ex. Candles, oil lamps, fireplace) Yes No N/A |  |  |
| W | Building has a history of any structure fire incidents: Yes No |  |  |
| X | Flammable and combustible liquids stored properly: Yes No N/A |  |  |
| Y | Is the building located within a wildland hazard fuel zone: Yes No |  |  |

| (2) Means of Egress (NFPA 101 Chapter 5) |  |
| --- | --- |
| A | Emergency Lights Required: Yes No Emergency Lights Provided: Yes No |
| B | Operable: Yes No Tested monthly: Yes No |
| C | Properly illuminates egress paths: Yes No In good visual condition: Yes No |
| D | Exit Signs Required: Yes No Exit Signs Provided: Yes No |
| E | Illuminated: internally externally Readily visible: Yes No |
| F | Properly located: Yes No |
| G | Egress Paths Readily Visible: Yes No Clear and Unobstructed: Yes No |
| H | Two remote exits available: Yes No N/A |
| I | Travel distance with in limits: Yes No |
| J | Common path of travel with in limits: Yes No |
| K | Dead ends with in limits: Yes No |
| L | Does more than 50% of the occupants exit through nonrated areas on level of exit discharge from rated stair enclosures: Yes No |
| (3) Fire Safety Construction (NFPA 101 Chapter 6) |  |
|  | #### Interior Finish |
| A | Noncombustible ceiling finish (Class A or B): Yes No |
| B | Noncombustible wall finish Class A or B): Yes No |
| C | Noncombustible floor finish (Class I or II): Yes No |
| D | Vertical Openings present: Yes No Properly protected/enclosed: Yes No |
| E | Atrium: Yes No Properly protected: Yes No |
| (4) Fire Protection Systems and Equipment (NFPA 101 Chapter 7) |  |
|  | Fire Extinguishers Required: Yes No Fire Extinguishers Provided: Yes No (NFPA 10) |
| A | Proper type for hazard being protected: Yes No |
| B | Mounted properly: Yes No |
| C | Number of extinguishers provided: _________ |
| D | Adequate number of extinguishers provided: Yes No |
| E | All extinguishers properly inspected and maintained annually: Yes No (NPFA 10, 4-3) |
| F | Are the extinguishers inspected monthly: Yes No (NPFA 10, 4-3) |
| (5) Fire Protection System (NFPA 101 Chapter 7) |  |
| A | Type of Suppression: None Sprinkler Halon CO2 Standpipes , Class ____ Water Spray Foam Dry chemical Wet chemical Other: _______________ |
| B | Sprinkler Systems Required: Yes No Sprinkler Systems Provided: Yes No |
| C | Coverage: Full Partial If partial indicate location: ______________________________ |
| D | System tested by: ___________________________________ Date of test: _______________ |
| E | Adequate clearance from storage and obstructions: Yes No If no, describe: |

| F | Are there other system deficiencies: Yes No If yes, describe: |  |
| --- | --- | --- |
| G | Valve Supervision: Electronic Tamper Switch Lock Seal Other: _________________ |  |
| H | Valves Accessible: Yes No |  |
| I | Kitchen Hood Systems R Required: Yes No Kitchen Hood Systems Provided: Yes No |  |
| J | Adequate Coverage: Yes No Cooking Areas not protected: ______________ |  |
| K | System tested by: __________________________________ Date of test: ___________ |  |
| L | Description of Specialized Protection Systems not already addressed: N/A ___________________________ |  |
| (6) Fire Detection and Alarm Systems (NFPA 101 Chapter 7) |  |  |
| A | Fire Alarm System Required: Yes No Fire Alarm System Provided: Yes No |  |
| B | System Type: Hardwired Addressable/Multiplex Radio/Wireless |  |
| C | Location of Fire Alarm Control Panel: _____________________________ |  |
| D | Location of Annunciator Panel: ____________________________ N/A |  |
| E | Monitored (Constantly Attended Location): Yes No |  |
| F | Occupant Notification Signal: Audible Only Audible/Visual None |  |
| G | Is Notification Audible in all areas: Yes No |  |
| H | Type of Initiation Devices: Smoke Heat Manual Pull Water flow Other: __________________ |  |
| I | System Smoke Detectors: Yes No Coverage: Full Partial |  |
| J | Single- or Multi- station smoke detectors: Yes No Operational with Battery Charged: Yes No |  |
| K | Alarm system devices ADA compliant: Yes No |  |
| L | Inspection and Test Records available: Yes No |  |
| M | Date of test: _____________ Date of inspection: ____________ Tested by: ______________ |  |
| (7) Fire Lanes (NFPA 1 Chapter 3 General Provisions, 3-5 Fire lanes) |  |  |
| A | Fire Lanes Required (150 from Road or 30 ft high & 50 from Road): Yes No |  |
| B | Fire Lanes Meet Minimum width (20 ft), height (13’-6”) and radius (50 ft): Yes No N/A |  |
| C | Fire Lanes Properly Marked: Yes No N/A |  |
| D | Fire Lanes Maintained and Free of Obstructions: Yes No N/A |  |
| ## Part IV Occupancy Fire Safety |  |
| (1) General Occupancy Information |  |
| A | Original Occupancy Classification (NFPA 101 Chapter 4): _________________________ |
| B | Current Occupancy Classification (NFPA 101 Chapter 4): _________________________ |
| C | Date of Construction: ______________ Date of last major renovation: N/A _______________ |
| D | Any renovations or modifications since last inspection: Yes No |
| E | Change of Occupancy or Classification from last inspection: Yes No N/A |
| F | Occupant load based on current Occupancy Classification (NFPA 101, Chapter 5): |
| G | Egress capacity (NFPA 101 Chapter 5): Adequate Inadequate |

| H |  | High Rise Building Yes No Windowless Building or Story: Yes No Underground Structure Yes No (NFPA 101 Chapter 3) |  |  |
| --- | --- | --- | --- | --- |
| (2) Assembly Occupancies (NFPA 1, Chapter 9): Yes N/A |  |  |  |  |
| A |  | Drills and employee instruction conducted: Yes No |  |  |
| B |  | Are open flame devices prohibited: Yes No |  |  |
| C |  | Non-flue portable cooking equipment prohibited: Yes No |  |  |
| D |  | Non-smoking areas are posted: Yes No |  |  |
| E |  | Furnishings, decorations, and scenery are flame resistant: Yes No |  |  |
| F |  | Seating in occupancies over 200 secured and in groups of 3-7: Yes No |  |  |
| G |  | Unsecured seating area is > 15 sq ft per seat: Yes No |  |  |
| H |  | Occupancy load posted in all areas with unsecured seating: Yes No |  |  |
| I |  | Projection room posted “Safety Film Only Permitted in this Room”: Yes No N/A |  |  |
| J |  | Clothing stored in corridors: Yes No |  |  |
| K |  | Crowd trained managers in assembly areas over 1000: Yes No N/A |  |  |
| (3) Dormitories (NFPA 1, Chapter 16): Yes N/A |  |  |  |  |
| A |  | Exit drills conducted regularly: Yes No |  |  |
| B |  | Drills designed in cooperation with local authorities: Yes No |  |  |
| C |  | Occupants familiar with drill procedure: Yes No |  |  |
| D |  | Competent person responsible for planning & conduct of drills: Yes No |  |  |
| E |  | Drills conducted in orderly and disciplined fashion: Yes No |  |  |
| F |  | Drills held at expected and unexpected times under varying conditions: Yes No |  |  |
| G |  | Floor diagram posted in each room and near exits: Yes No |  |  |
| H |  | Fire safety information posted for evacuation options: Yes No |  |  |
| I |  | Draperies and curtains are flame resistant: Yes No |  |  |
| J |  | Unvented fuel- fired heaters in use: Yes No |  |  |
| (4) Business Occupancies (NFPA 1, Chapter 21): Yes N/A |  |  |  |  |  |
| A |  | Occupancy > 500 total or >100 above or below street level? Yes No |  |  |  |
| B |  | Periodic employee fire drill instruction? Yes No Date of last instruction: _________________ |  |  |  |
| C |  | Periodic fire drills conducted? Yes No Date of last fire drill: _________________ |  |  |  |
| D |  | Periodic employee fire extinguisher instruction? Yes No Date of last instruction: _________________ |  |  |  |
| (5) Industrial Occupancies (NFPA 1, Chapter 22) Yes N/A |  |  |  |  |  |
| A |  | Service stations: Yes N/A |  |  |  |
| B |  | Storage requirements met: Yes No (NFPA 1, 22-2.2) |  |  |  |
| C |  | Piping, valves, and fittings requirements met: Yes No (NFPA 1, 22.2-3) |  |  |  |
| D |  | Fuel dispensing system requirements met: Yes No (NFPA 1, 22.2-4) |  |  |  |
| E |  | Service station located within buildings requirements met: Yes No N/A (NFPA 1, 22.2-5) |  |  |  |
| F |  | Electrical equipment requirements met: Yes No (NFPA 1, 22.2-6) |  |  |  |
| G |  | Heat producing appliances requirements met: Yes No (NFPA 1, 22.2-7) |  |  |  |
| H |  | Operational requirements met: Yes No (NFPA 1, 22.2-8) |  |  |  |
| I |  | Marine service station requirements met: Yes No (NFPA 1, 22.2-9) |  |  |  |
| J |  | Below grade and subfloor work area requirements met: Yes No (NFPA 1, 22.2-10) |  |  |  |
| K |  | Repair garages: Yes N/A |  |  |  |
| L |  | Construction requirements met: Yes No (NFPA 1, 22.3-2) |  |  |  |
| M |  | Hazard control requirements met: Yes No (NFPA 1, 22.3-3) |  |  |  |
| N |  | Protection requirements met: Yes No (NFPA 1, 22.3-4) |  |  |  |
| O |  | Dry cleaning plants: Yes N/A Complies with NFPA 32: Yes No |  |  |  |
| (6) Storage Occupancies (NFPA 1, Chapter 23) Yes N/A |  |  |  |
| A |  | General storage up to 30 feet: Yes N/A Complies with NFPA 230 Yes No |  |
| B |  | Rack storage over 12 feet: Yes N/A Complies with NFPA 230 Yes No |  |
| C |  | Aircraft hangars: Yes N/A Complies with NFPA 409 Yes No |  |
| D |  | Bulk storage elevators: Yes N/A Complies with NFPA 61 Yes No |  |
| E |  | Parking garages: Yes N/A Complies with NFPA 88A Yes No |  |
| F |  | Tire storage: Yes N/A Complies with NFPA 231D Yes No |  |
| ## Part V Special Processes and Materials Handling |  |  |
| Where applicable, special processes and materials handling shall comply with the corresponding, Chapter of NFPA 1 |  |  |
| A |  | Oxidizers and organic peroxides: Yes N/A Complies with Chapter 27: Yes No |
| B |  | Flammable and combustible liquids: Yes N/A Complies with Chapter 28: Yes No |
| C |  | Aerosol products: Yes N/A Complies with Chapter 29: Yes No |
| D |  | LPG/LNG: Yes N/A Complies with Chapter 30: Yes No |
| E |  | Fireworks/pyrotechnics: Yes N/A Complies with Chapter 31: Yes No |
| F |  | Heating appliances: Yes N/A Complies with Chapter 32: Yes No |
| G |  | Spray application of flammables: Yes N/A Complies with Chapter 33: Yes No |
| H |  | Welding and cutting/hot work: Yes N/A Complies with Chapter 34: Yes No |
| I |  | Dust explosion hazard: Yes N/A Complies with Chapter 35: Yes No |
| J |  | Industrial ovens and furnaces: Yes N/A Complies with Chapter 36: Yes No |
| K |  | Mechanical refrigeration: Yes N/A Complies with Chapter 37: Yes No |
| L |  | Explosive materials: Yes N/A Complies with Chapter 38: Yes No |
| M |  | Combustible fibers: Yes N/A Complies with Chapter 39: Yes No |
| N |  | Refueling: Yes N/A Complies with Chapter 40: Yes No |
| O |  | Construction and demolition: Yes N/A Complies with Chapter 41: Yes No |
| ## Part VI Fire Suppression Response |  |  |
| (1) Water Supply |  |  |
| A | Required GPM: __________ Meets minimum GPM requirements: Yes No (ISO calculation method) Required volume (GPM x 90 Min.):____________ Meets minimum volume needs: Yes No |  |
| (2) Fire Services |  |  |
| A | Primary response by local fire department: Yes No |  |
| B | Primary responding agency: Yes No |  |
| C | Current written and signed structural fire agreement in place (provide copy if available): Yes No |  |
| D | Building preplans complete and current: Yes No |  |
| E | Are responding resources knowledgeable of property and value: Yes No |  |
| (3) Primary Responding Department/Brigade: |  |  |  |
| A | Response time (time to most remote building): |  |  |
| B | Permanently organized under one chief: Yes No |  |  |
| C | Is the area of response defined and supported by Fire Dept. Management: Yes No |  |  |
| D | Adequately staffed (minimum of 4) for initial attack response: Day: Yes No Night: Yes No |  |  |
| E | Is the incident management system utilized for all emergency responses: Yes No |  |  |
| F | Are members/officers trained in incident management procedures: Yes No |  |  |
| G | Does personal protective equipment meet NFPA 1971 requirements: Yes No |  |  |
| H | Personal protective equipment properly maintained and available for response: Yes No |  |  |
| I | Does fire apparatus meet NFPA 1901 requirements: Yes No |  |  |
| J | Apparatus capable of pumping required water supply: Yes No |  |  |
| K | Apparatus properly maintained and available for response: Yes No |  |  |
| L | Training standards meet NFPA 1001, 1021 requirements: Yes No |  |  |
| NOTE: | Primary Codes to be used are 1997 Edition of NFPA 1, Fire Prevention Code and 1997 Edition of NFPA 101, Life Safety Code. |  |  |

| Section # | Comments |
| --- | --- |

Contact OSHMB if you require additional assistance.